## Sheet1
Chronology of Events Associated with RD 2035 Pump 27 Failure
Date | Observations | Action
2025-02-11 | District personnel observed that the Concrete Surge Box of Pump 27 had shifted several feet toward the drainage ditch and separated from the main 60-inch discharge corrugated metal pipe. The flow pipes connected to the vertical pumps were also damaged and detached. As a result, water from the Yolo Bypass began flowing into the drainage ditch on the landside of the levee. RD 2035 personnel attempted to close the slide gate valve on the water side of the levee but were unsuccessful. See attached photos for further details. | The GM informed the Board President and the District Engineer. The District Engineer notified the Flood Center and requested DWR's technical assistance. A meeting was held on-site with RD, DWR, Wood Rodgers personnel, and Construction Contractor JD Pasquetti to discuss the situation and take action to address the emergency. To stop the flow, RD 2035 placed several super sacks (containing sand and cement) into the slide gate riser. However, this attempt was unsuccessful, and water continued to flow from the Yolo Bypass into the drainage ditch along the west levee. A decision was made to continue monitoring the situation and meet again on 2/12 to discuss next steps. It was also decided to install four temporary submersible pumps on an emergency basis to maintain drainage operations and pump water back into the Yolo Bypass.
2025-02-12 | A meeting was held on-site at 8:00 AM with DWR, RD 2035/Conaway, JD Pasquetti, and Wood Rodgers. The decision was made to construct a coffer dam at the headwall of the damaged pipe, lay the filter fabric and fill the hole next to the collapsed pump station structure with riprap, and cover the levee section with plastic. | We placed a large quantity of riprap and aggregate base at the mouth of the damaged pipe's headwall on the Yolo Bypass side. Filter fabric and riprap were installed next to the pump structure to reduce erosion. Additionally, the upstream portion of the levee was covered with Visqueen to protect it from rainwater saturation and prevent added load. Work began on installing temporary submersible pumps.
2025-02-13 | The temporary measures reduced the flow of water coming from the Yolo Bypass into the drainage ditch, but did not stop it completely. Based on the observation that the temporary measures would prevent further damage to the levee, the District Engineer recommended to the GM and Board President not to install sheet piles to completely cut off the flow of water from the Yolo Bypass. The District Engineer also recommended requesting direct assistance from DWR to assess whether further action was needed to stop the flow of water into the drainage ditch. | The GM and Board President approved the District Engineer's recommendation. Consequently, the decision was made not to pursue the installation of sheet piles, and a request for direct assistance from DWR was submitted. The purpose of this request was to keep DWR engaged, ensuring that if the situation worsened, they could take over emergency operations. Additionally, the CVFPB was informed that temporary pumps were being installed.
2025-02-14 | Continued monitoring of the situation and temporary measures in place to protect the levee’s integrity. | The District Engineer recommended to the GM to declare an emergency in accordance with RD 2035’s Emergency Operations Plan (EOP).